## Target & Actual Superheat
Indoor air WB temperature at return air intake | 65 | ⁰F (wetbulb) | Measure the wetbulb temperature of the air flowing into indoor return air intake and enter it here (See Notes).
Outdoor air DB Temperature at condenser intake | 93 | ⁰F (drybulb) | Measure the drybulb temperature of the air flowing into the outdoor condenser and enter it here (See Notes).
Target superheat | 11 | ⁰F | This is the calculated target superheat based upon the previous measurements.
Suction line temperature | 60 | ⁰F | Measure the temperature of the suction line at the condenser and enter it here.
Suction line pressure | 80 | psig | Measure the pressure of the suction line at the condenser and enter it here.
Actual superheat | 12.4572 | ⁰F | This is the actual superheat based upon the previous measurements. Add charge to increase, remove charge to decrease.
Target suction line temperature @ 80 psig | 58.5428 | ⁰F | This is the temperature goal of the suction line for the target superheat at the measured pressure. (This will change with pressure).
All measurements to be performed while the system is running/cooling.
Air temperature measurements are to be made in the flowing air stream.

## Target Superheat Chart
Condenser DB
Indoor WB | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100
60 | 15 | 14.5 | 14 | 13.5 | 13 | 12.5 | 12 | 11.5 | 11 | 10.5 | 10 | 9.5 | 9 | 8.5 | 8 | 7.5 | 7 | 6.5 | 6 | 5.5 | 5 | 4.5 | 4 | 3.5 | 3 | 2.5 | 2 | 1.5 | 1 | 0.5 | 0
61 | 16.5 | 16 | 15.5 | 15 | 14.5 | 14 | 13.5 | 13 | 12.5 | 12 | 11.5 | 11 | 10.5 | 10 | 9.5 | 9 | 8.5 | 8 | 7.5 | 7 | 6.5 | 6 | 5.5 | 5 | 4.5 | 4 | 3.5 | 3 | 2.5 | 2 | 1.5
62 | 18 | 17.5 | 17 | 16.5 | 16 | 15.5 | 15 | 14.5 | 14 | 13.5 | 13 | 12.5 | 12 | 11.5 | 11 | 10.5 | 10 | 9.5 | 9 | 8.5 | 8 | 7.5 | 7 | 6.5 | 6 | 5.5 | 5 | 4.5 | 4 | 3.5 | 3
63 | 19.5 | 19 | 18.5 | 18 | 17.5 | 17 | 16.5 | 16 | 15.5 | 15 | 14.5 | 14 | 13.5 | 13 | 12.5 | 12 | 11.5 | 11 | 10.5 | 10 | 9.5 | 9 | 8.5 | 8 | 7.5 | 7 | 6.5 | 6 | 5.5 | 5 | 4.5
64 | 21 | 20.5 | 20 | 19.5 | 19 | 18.5 | 18 | 17.5 | 17 | 16.5 | 16 | 15.5 | 15 | 14.5 | 14 | 13.5 | 13 | 12.5 | 12 | 11.5 | 11 | 10.5 | 10 | 9.5 | 9 | 8.5 | 8 | 7.5 | 7 | 6.5 | 6
65 | 22.5 | 22 | 21.5 | 21 | 20.5 | 20 | 19.5 | 19 | 18.5 | 18 | 17.5 | 17 | 16.5 | 16 | 15.5 | 15 | 14.5 | 14 | 13.5 | 13 | 12.5 | 12 | 11.5 | 11 | 10.5 | 10 | 9.5 | 9 | 8.5 | 8 | 7.5
66 | 24 | 23.5 | 23 | 22.5 | 22 | 21.5 | 21 | 20.5 | 20 | 19.5 | 19 | 18.5 | 18 | 17.5 | 17 | 16.5 | 16 | 15.5 | 15 | 14.5 | 14 | 13.5 | 13 | 12.5 | 12 | 11.5 | 11 | 10.5 | 10 | 9.5 | 9
67 | 25.5 | 25 | 24.5 | 24 | 23.5 | 23 | 22.5 | 22 | 21.5 | 21 | 20.5 | 20 | 19.5 | 19 | 18.5 | 18 | 17.5 | 17 | 16.5 | 16 | 15.5 | 15 | 14.5 | 14 | 13.5 | 13 | 12.5 | 12 | 11.5 | 11 | 10.5
68 | 27 | 26.5 | 26 | 25.5 | 25 | 24.5 | 24 | 23.5 | 23 | 22.5 | 22 | 21.5 | 21 | 20.5 | 20 | 19.5 | 19 | 18.5 | 18 | 17.5 | 17 | 16.5 | 16 | 15.5 | 15 | 14.5 | 14 | 13.5 | 13 | 12.5 | 12
69 | 28.5 | 28 | 27.5 | 27 | 26.5 | 26 | 25.5 | 25 | 24.5 | 24 | 23.5 | 23 | 22.5 | 22 | 21.5 | 21 | 20.5 | 20 | 19.5 | 19 | 18.5 | 18 | 17.5 | 17 | 16.5 | 16 | 15.5 | 15 | 14.5 | 14 | 13.5
70 | 30 | 29.5 | 29 | 28.5 | 28 | 27.5 | 27 | 26.5 | 26 | 25.5 | 25 | 24.5 | 24 | 23.5 | 23 | 22.5 | 22 | 21.5 | 21 | 20.5 | 20 | 19.5 | 19 | 18.5 | 18 | 17.5 | 17 | 16.5 | 16 | 15.5 | 15
71 | 31.5 | 31 | 30.5 | 30 | 29.5 | 29 | 28.5 | 28 | 27.5 | 27 | 26.5 | 26 | 25.5 | 25 | 24.5 | 24 | 23.5 | 23 | 22.5 | 22 | 21.5 | 21 | 20.5 | 20 | 19.5 | 19 | 18.5 | 18 | 17.5 | 17 | 16.5
72 | 33 | 32.5 | 32 | 31.5 | 31 | 30.5 | 30 | 29.5 | 29 | 28.5 | 28 | 27.5 | 27 | 26.5 | 26 | 25.5 | 25 | 24.5 | 24 | 23.5 | 23 | 22.5 | 22 | 21.5 | 21 | 20.5 | 20 | 19.5 | 19 | 18.5 | 18
73 | 34.5 | 34 | 33.5 | 33 | 32.5 | 32 | 31.5 | 31 | 30.5 | 30 | 29.5 | 29 | 28.5 | 28 | 27.5 | 27 | 26.5 | 26 | 25.5 | 25 | 24.5 | 24 | 23.5 | 23 | 22.5 | 22 | 21.5 | 21 | 20.5 | 20 | 19.5
74 | 36 | 35.5 | 35 | 34.5 | 34 | 33.5 | 33 | 32.5 | 32 | 31.5 | 31 | 30.5 | 30 | 29.5 | 29 | 28.5 | 28 | 27.5 | 27 | 26.5 | 26 | 25.5 | 25 | 24.5 | 24 | 23.5 | 23 | 22.5 | 22 | 21.5 | 21
75 | 37.5 | 37 | 36.5 | 36 | 35.5 | 35 | 34.5 | 34 | 33.5 | 33 | 32.5 | 32 | 31.5 | 31 | 30.5 | 30 | 29.5 | 29 | 28.5 | 28 | 27.5 | 27 | 26.5 | 26 | 25.5 | 25 | 24.5 | 24 | 23.5 | 23 | 22.5
76 | 39 | 38.5 | 38 | 37.5 | 37 | 36.5 | 36 | 35.5 | 35 | 34.5 | 34 | 33.5 | 33 | 32.5 | 32 | 31.5 | 31 | 30.5 | 30 | 29.5 | 29 | 28.5 | 28 | 27.5 | 27 | 26.5 | 26 | 25.5 | 25 | 24.5 | 24
77 | 40.5 | 40 | 39.5 | 39 | 38.5 | 38 | 37.5 | 37 | 36.5 | 36 | 35.5 | 35 | 34.5 | 34 | 33.5 | 33 | 32.5 | 32 | 31.5 | 31 | 30.5 | 30 | 29.5 | 29 | 28.5 | 28 | 27.5 | 27 | 26.5 | 26 | 25.5
78 | 42 | 41.5 | 41 | 40.5 | 40 | 39.5 | 39 | 38.5 | 38 | 37.5 | 37 | 36.5 | 36 | 35.5 | 35 | 34.5 | 34 | 33.5 | 33 | 32.5 | 32 | 31.5 | 31 | 30.5 | 30 | 29.5 | 29 | 28.5 | 28 | 27.5 | 27
79 | 43.5 | 43 | 42.5 | 42 | 41.5 | 41 | 40.5 | 40 | 39.5 | 39 | 38.5 | 38 | 37.5 | 37 | 36.5 | 36 | 35.5 | 35 | 34.5 | 34 | 33.5 | 33 | 32.5 | 32 | 31.5 | 31 | 30.5 | 30 | 29.5 | 29 | 28.5
80 | 45 | 44.5 | 44 | 43.5 | 43 | 42.5 | 42 | 41.5 | 41 | 40.5 | 40 | 39.5 | 39 | 38.5 | 38 | 37.5 | 37 | 36.5 | 36 | 35.5 | 35 | 34.5 | 34 | 33.5 | 33 | 32.5 | 32 | 31.5 | 31 | 30.5 | 30
81 | 46.5 | 46 | 45.5 | 45 | 44.5 | 44 | 43.5 | 43 | 42.5 | 42 | 41.5 | 41 | 40.5 | 40 | 39.5 | 39 | 38.5 | 38 | 37.5 | 37 | 36.5 | 36 | 35.5 | 35 | 34.5 | 34 | 33.5 | 33 | 32.5 | 32 | 31.5
82 | 48 | 47.5 | 47 | 46.5 | 46 | 45.5 | 45 | 44.5 | 44 | 43.5 | 43 | 42.5 | 42 | 41.5 | 41 | 40.5 | 40 | 39.5 | 39 | 38.5 | 38 | 37.5 | 37 | 36.5 | 36 | 35.5 | 35 | 34.5 | 34 | 33.5 | 33
83 | 49.5 | 49 | 48.5 | 48 | 47.5 | 47 | 46.5 | 46 | 45.5 | 45 | 44.5 | 44 | 43.5 | 43 | 42.5 | 42 | 41.5 | 41 | 40.5 | 40 | 39.5 | 39 | 38.5 | 38 | 37.5 | 37 | 36.5 | 36 | 35.5 | 35 | 34.5
84 | 51 | 50.5 | 50 | 49.5 | 49 | 48.5 | 48 | 47.5 | 47 | 46.5 | 46 | 45.5 | 45 | 44.5 | 44 | 43.5 | 43 | 42.5 | 42 | 41.5 | 41 | 40.5 | 40 | 39.5 | 39 | 38.5 | 38 | 37.5 | 37 | 36.5 | 36
85 | 52.5 | 52 | 51.5 | 51 | 50.5 | 50 | 49.5 | 49 | 48.5 | 48 | 47.5 | 47 | 46.5 | 46 | 45.5 | 45 | 44.5 | 44 | 43.5 | 43 | 42.5 | 42 | 41.5 | 41 | 40.5 | 40 | 39.5 | 39 | 38.5 | 38 | 37.5

## R22 PT Calcs
Charting the Equation
Sat [⁰F] | Sat [⁰R] | psia | psig
-51 | 408.67 | 11.3524 | -3.3436
-50 | 409.67 | 11.6673 | -3.0287
-49 | 410.67 | 11.989 | -2.707
-48 | 411.67 | 12.3178 | -2.3782
-47 | 412.67 | 12.6537 | -2.0423
-46 | 413.67 | 12.9968 | -1.6992
-45 | 414.67 | 13.3473 | -1.3487
-44 | 415.67 | 13.7052 | -0.99078
-43 | 416.67 | 14.0707 | -0.62527
-42 | 417.67 | 14.4439 | -0.25208 | Mastering the equation
-41 | 418.67 | 14.8249 | 0.1289 | Sat T [⁰F] | SatT [⁰R] | psia | psig | psig from dupont chart
-40 | 419.67 | 15.2138 | 0.51779 | 60 | 519.67 | 116.2745 | 101.5785 | 101.6
-39 | 420.67 | 15.6107 | 0.91471 | 70 | 529.67 | 136.0807 | 121.3847 | 121.4
-38 | 421.67 | 16.0158 | 1.3198 | 80 | 539.67 | 158.2793 | 143.5833 | 143.6
-37 | 422.67 | 16.4291 | 1.7331 | 90 | 549.67 | 183.0419 | 168.3459 | 168.4
-36 | 423.67 | 16.8507 | 2.1547 | 100 | 559.67 | 210.5464 | 195.8504 | 195.9
-35 | 424.67 | 17.2809 | 2.5849
-34 | 425.67 | 17.7196 | 3.0236 | Solving for temperature using bisection method
-33 | 426.67 | 18.1671 | 3.4711 | psig | 80 |  | Sat [⁰F] | 47.5428
-32 | 427.67 | 18.6234 | 3.9274 | psia | 94.696
-31 | 428.67 | 19.0887 | 4.3927 | Sat [⁰R] Lo | Sat [⁰R] Hi | psia Lo | psia Hi | Sat [⁰R] Mid | psia Mid |  | Error | Next Sat [⁰R] Lo | Next Sat [⁰R] Hi
-30 | 429.67 | 19.563 | 4.867 | 418 | 685 | 14.5688 | 898.4515 | 551.5 | 187.8649 | OVER | 98.39% | 418 | 551.5
-29 | 430.67 | 20.0466 | 5.3506 | 418 | 551.5 | 14.5688 | 187.8649 | 484.75 | 63.5207 | UNDER | -32.92% | 484.75 | 551.5
-28 | 431.67 | 20.5395 | 5.8435 | 484.75 | 551.5 | 63.5207 | 187.8649 | 518.125 | 113.4171 | OVER | 19.77% | 484.75 | 518.125
-27 | 432.67 | 21.0418 | 6.3458 | 484.75 | 518.125 | 63.5207 | 113.4171 | 501.4375 | 85.7766 | UNDER | -9.419% | 501.4375 | 518.125
-26 | 433.67 | 21.5537 | 6.8577 | 501.4375 | 518.125 | 85.7766 | 113.4171 | 509.7812 | 98.878 | OVER | 4.416% | 501.4375 | 509.7812
-25 | 434.67 | 22.0753 | 7.3793 | 501.4375 | 509.7812 | 85.7766 | 98.878 | 505.6094 | 92.1534 | UNDER | -2.685% | 505.6094 | 509.7812
-24 | 435.67 | 22.6067 | 7.9107 | 505.6094 | 509.7812 | 92.1534 | 98.878 | 507.6953 | 95.4715 | OVER | 0.8189% | 505.6094 | 507.6953
-23 | 436.67 | 23.148 | 8.452 | 505.6094 | 507.6953 | 92.1534 | 95.4715 | 506.6523 | 93.8015 | UNDER | -0.9446% | 506.6523 | 507.6953
-22 | 437.67 | 23.6994 | 9.0034 | 506.6523 | 507.6953 | 93.8015 | 95.4715 | 507.1738 | 94.6337 | UNDER | -0.06576% | 507.1738 | 507.6953
-21 | 438.67 | 24.261 | 9.565 | 507.1738 | 507.6953 | 94.6337 | 95.4715 | 507.4346 | 95.0519 | OVER | 0.3759% | 507.1738 | 507.4346
-20 | 439.67 | 24.833 | 10.137 | 507.1738 | 507.4346 | 94.6337 | 95.0519 | 507.3042 | 94.8427 | OVER | 0.1549% | 507.1738 | 507.3042
-19 | 440.67 | 25.4153 | 10.7193 | 507.1738 | 507.3042 | 94.6337 | 94.8427 | 507.239 | 94.7381 | OVER | 0.04451% | 507.1738 | 507.239
-18 | 441.67 | 26.0083 | 11.3123 | 507.1738 | 507.239 | 94.6337 | 94.7381 | 507.2064 | 94.6859 | UNDER | -0.01064% | 507.2064 | 507.239
-17 | 442.67 | 26.612 | 11.916 | 507.2064 | 507.239 | 94.6859 | 94.7381 | 507.2227 | 94.712 | OVER | 0.01693% | 507.2064 | 507.2227
-16 | 443.67 | 27.2265 | 12.5305 | 507.2064 | 507.2227 | 94.6859 | 94.712 | 507.2146 | 94.699 | OVER | 0.003147% | 507.2064 | 507.2146
-15 | 444.67 | 27.8519 | 13.1559 | 507.2064 | 507.2146 | 94.6859 | 94.699 | 507.2105 | 94.6925 | UNDER | -0.003745% | 507.2105 | 507.2146
-14 | 445.67 | 28.4885 | 13.7925 | 507.2105 | 507.2146 | 94.6925 | 94.699 | 507.2125 | 94.6957 | UNDER | -0.0002988% | 507.2125 | 507.2146
-13 | 446.67 | 29.1363 | 14.4403 | 507.2125 | 507.2146 | 94.6957 | 94.699 | 507.2136 | 94.6973 | OVER | 0.001424% | 507.2125 | 507.2136
-12 | 447.67 | 29.7955 | 15.0995 | 507.2125 | 507.2136 | 94.6957 | 94.6973 | 507.213 | 94.6965 | OVER | 0.0005627% | 507.2125 | 507.213
-11 | 448.67 | 30.4661 | 15.7701 | 507.2125 | 507.213 | 94.6957 | 94.6965 | 507.2128 | 94.6961 | OVER | 0.0001319% | 507.2125 | 507.2128
-10 | 449.67 | 31.1484 | 16.4524
-9 | 450.67 | 31.8424 | 17.1464
-8 | 451.67 | 32.5484 | 17.8524
-7 | 452.67 | 33.2663 | 18.5703
-6 | 453.67 | 33.9965 | 19.3005
-5 | 454.67 | 34.7389 | 20.0429
-4 | 455.67 | 35.4938 | 20.7978
-3 | 456.67 | 36.2612 | 21.5652
-2 | 457.67 | 37.0413 | 22.3453
-1 | 458.67 | 37.8343 | 23.1383
0 | 459.67 | 38.6403 | 23.9443
1 | 460.67 | 39.4594 | 24.7634
2 | 461.67 | 40.2918 | 25.5958
3 | 462.67 | 41.1376 | 26.4416
4 | 463.67 | 41.9969 | 27.3009
5 | 464.67 | 42.87 | 28.174
6 | 465.67 | 43.7568 | 29.0608
7 | 466.67 | 44.6576 | 29.9616
8 | 467.67 | 45.5726 | 30.8766
9 | 468.67 | 46.5018 | 31.8058
10 | 469.67 | 47.4453 | 32.7493
11 | 470.67 | 48.4035 | 33.7075
12 | 471.67 | 49.3763 | 34.6803
13 | 472.67 | 50.3639 | 35.6679
14 | 473.67 | 51.3666 | 36.6706
15 | 474.67 | 52.3843 | 37.6883
16 | 475.67 | 53.4173 | 38.7213
17 | 476.67 | 54.4658 | 39.7698
18 | 477.67 | 55.5298 | 40.8338
19 | 478.67 | 56.6095 | 41.9135
20 | 479.67 | 57.705 | 43.009
21 | 480.67 | 58.8166 | 44.1206
22 | 481.67 | 59.9443 | 45.2483
23 | 482.67 | 61.0883 | 46.3923
24 | 483.67 | 62.2488 | 47.5528
25 | 484.67 | 63.4259 | 48.7299
26 | 485.67 | 64.6197 | 49.9237
27 | 486.67 | 65.8304 | 51.1344
28 | 487.67 | 67.0582 | 52.3622
29 | 488.67 | 68.3032 | 53.6072
30 | 489.67 | 69.5655 | 54.8695
31 | 490.67 | 70.8453 | 56.1493
32 | 491.67 | 72.1429 | 57.4469
33 | 492.67 | 73.4582 | 58.7622
34 | 493.67 | 74.7915 | 60.0955
35 | 494.67 | 76.1429 | 61.4469
36 | 495.67 | 77.5125 | 62.8165
37 | 496.67 | 78.9006 | 64.2046
38 | 497.67 | 80.3073 | 65.6113
39 | 498.67 | 81.7328 | 67.0368
40 | 499.67 | 83.1771 | 68.4811
41 | 500.67 | 84.6405 | 69.9445
42 | 501.67 | 86.123 | 71.427
43 | 502.67 | 87.625 | 72.929
44 | 503.67 | 89.1465 | 74.4505
45 | 504.67 | 90.6876 | 75.9916
46 | 505.67 | 92.2486 | 77.5526
47 | 506.67 | 93.8296 | 79.1336
48 | 507.67 | 95.4307 | 80.7347
49 | 508.67 | 97.0521 | 82.3561
50 | 509.67 | 98.694 | 83.998
51 | 510.67 | 100.3566 | 85.6606
52 | 511.67 | 102.0399 | 87.3439
53 | 512.67 | 103.7442 | 89.0482
54 | 513.67 | 105.4696 | 90.7736
55 | 514.67 | 107.2163 | 92.5203
56 | 515.67 | 108.9844 | 94.2884
57 | 516.67 | 110.7741 | 96.0781
58 | 517.67 | 112.5856 | 97.8896
59 | 518.67 | 114.419 | 99.723
60 | 519.67 | 116.2745 | 101.5785
61 | 520.67 | 118.1523 | 103.4563
62 | 521.67 | 120.0524 | 105.3564
63 | 522.67 | 121.9752 | 107.2792
64 | 523.67 | 123.9207 | 109.2247
65 | 524.67 | 125.8891 | 111.1931
66 | 525.67 | 127.8806 | 113.1846
67 | 526.67 | 129.8953 | 115.1993
68 | 527.67 | 131.9335 | 117.2375
69 | 528.67 | 133.9952 | 119.2992
70 | 529.67 | 136.0807 | 121.3847
71 | 530.67 | 138.1901 | 123.4941
72 | 531.67 | 140.3236 | 125.6276
73 | 532.67 | 142.4814 | 127.7854
74 | 533.67 | 144.6636 | 129.9676
75 | 534.67 | 146.8703 | 132.1743
76 | 535.67 | 149.1019 | 134.4059
77 | 536.67 | 151.3584 | 136.6624
78 | 537.67 | 153.64 | 138.944
79 | 538.67 | 155.9469 | 141.2509
80 | 539.67 | 158.2793 | 143.5833
81 | 540.67 | 160.6372 | 145.9412
82 | 541.67 | 163.0211 | 148.3251
83 | 542.67 | 165.4308 | 150.7348
84 | 543.67 | 167.8668 | 153.1708
85 | 544.67 | 170.3291 | 155.6331
86 | 545.67 | 172.8179 | 158.1219
87 | 546.67 | 175.3334 | 160.6374
88 | 547.67 | 177.8758 | 163.1798
89 | 548.67 | 180.4452 | 165.7492
90 | 549.67 | 183.0419 | 168.3459
91 | 550.67 | 185.6659 | 170.9699
92 | 551.67 | 188.3176 | 173.6216
93 | 552.67 | 190.9971 | 176.3011
94 | 553.67 | 193.7045 | 179.0085
95 | 554.67 | 196.44 | 181.744
96 | 555.67 | 199.2039 | 184.5079
97 | 556.67 | 201.9963 | 187.3003
98 | 557.67 | 204.8174 | 190.1214
99 | 558.67 | 207.6674 | 192.9714
100 | 559.67 | 210.5464 | 195.8504
101 | 560.67 | 213.4548 | 198.7588
102 | 561.67 | 216.3926 | 201.6966
103 | 562.67 | 219.36 | 204.664
104 | 563.67 | 222.3573 | 207.6613
105 | 564.67 | 225.3846 | 210.6886
106 | 565.67 | 228.4421 | 213.7461
107 | 566.67 | 231.5301 | 216.8341
108 | 567.67 | 234.6487 | 219.9527
109 | 568.67 | 237.7981 | 223.1021
110 | 569.67 | 240.9785 | 226.2825
111 | 570.67 | 244.1901 | 229.4941
112 | 571.67 | 247.4332 | 232.7372
113 | 572.67 | 250.7079 | 236.0119
114 | 573.67 | 254.0144 | 239.3184
115 | 574.67 | 257.3529 | 242.6569
116 | 575.67 | 260.7237 | 246.0277
117 | 576.67 | 264.1269 | 249.4309
118 | 577.67 | 267.5627 | 252.8667
119 | 578.67 | 271.0315 | 256.3355
120 | 579.67 | 274.5333 | 259.8373
121 | 580.67 | 278.0684 | 263.3724
122 | 581.67 | 281.637 | 266.941
123 | 582.67 | 285.2393 | 270.5433
124 | 583.67 | 288.8756 | 274.1796
125 | 584.67 | 292.5461 | 277.8501
126 | 585.67 | 296.2509 | 281.5549
127 | 586.67 | 299.9903 | 285.2943
128 | 587.67 | 303.7646 | 289.0686
129 | 588.67 | 307.574 | 292.878
130 | 589.67 | 311.4186 | 296.7226
131 | 590.67 | 315.2988 | 300.6028
132 | 591.67 | 319.2148 | 304.5188
133 | 592.67 | 323.1668 | 308.4708
134 | 593.67 | 327.155 | 312.459
135 | 594.67 | 331.1797 | 316.4837
136 | 595.67 | 335.2411 | 320.5451
137 | 596.67 | 339.3395 | 324.6435
138 | 597.67 | 343.4751 | 328.7791
139 | 598.67 | 347.6483 | 332.9523
140 | 599.67 | 351.8591 | 337.1631
141 | 600.67 | 356.108 | 341.412
142 | 601.67 | 360.3951 | 345.6991
143 | 602.67 | 364.7207 | 350.0247
144 | 603.67 | 369.0851 | 354.3891
145 | 604.67 | 373.4886 | 358.7926
146 | 605.67 | 377.9314 | 363.2354
147 | 606.67 | 382.4138 | 367.7178
148 | 607.67 | 386.9361 | 372.2401
149 | 608.67 | 391.4986 | 376.8026
150 | 609.67 | 396.1016 | 381.4056
151 | 610.67 | 400.7454 | 386.0494
152 | 611.67 | 405.4302 | 390.7342
153 | 612.67 | 410.1563 | 395.4603
154 | 613.67 | 414.9242 | 400.2282
155 | 614.67 | 419.734 | 405.038
156 | 615.67 | 424.5861 | 409.8901
157 | 616.67 | 429.4808 | 414.7848
158 | 617.67 | 434.4185 | 419.7225
159 | 618.67 | 439.3995 | 424.7035
160 | 619.67 | 444.4241 | 429.7281
161 | 620.67 | 449.4927 | 434.7967
162 | 621.67 | 454.6056 | 439.9096
163 | 622.67 | 459.7631 | 445.0671
164 | 623.67 | 464.9657 | 450.2697
165 | 624.67 | 470.2138 | 455.5178
166 | 625.67 | 475.5076 | 460.8116
167 | 626.67 | 480.8476 | 466.1516
168 | 627.67 | 486.2341 | 471.5381
169 | 628.67 | 491.6677 | 476.9717
170 | 629.67 | 497.1486 | 482.4526
171 | 630.67 | 502.6774 | 487.9814
172 | 631.67 | 508.2544 | 493.5584
173 | 632.67 | 513.88 | 499.184
174 | 633.67 | 519.5549 | 504.8589
175 | 634.67 | 525.2793 | 510.5833
176 | 635.67 | 531.0538 | 516.3578
177 | 636.67 | 536.8789 | 522.1829
178 | 637.67 | 542.7551 | 528.0591
179 | 638.67 | 548.6829 | 533.9869
180 | 639.67 | 554.6628 | 539.9668
181 | 640.67 | 560.6954 | 545.9994
182 | 641.67 | 566.7812 | 552.0852
183 | 642.67 | 572.9209 | 558.2249
184 | 643.67 | 579.115 | 564.419
185 | 644.67 | 585.3641 | 570.6681
186 | 645.67 | 591.6689 | 576.9729
187 | 646.67 | 598.0301 | 583.3341
188 | 647.67 | 604.4483 | 589.7523
189 | 648.67 | 610.9243 | 596.2283
190 | 649.67 | 617.4589 | 602.7629
191 | 650.67 | 624.0527 | 609.3567
192 | 651.67 | 630.7066 | 616.0106
193 | 652.67 | 637.4215 | 622.7255
194 | 653.67 | 644.1982 | 629.5022
195 | 654.67 | 651.0377 | 636.3417
196 | 655.67 | 657.9409 | 643.2449
197 | 656.67 | 664.9088 | 650.2128
198 | 657.67 | 671.9426 | 657.2466
199 | 658.67 | 679.0433 | 664.3473
200 | 659.67 | 686.2122 | 671.5162
201 | 660.67 | 693.4505 | 678.7545
202 | 661.67 | 700.7596 | 686.0636
203 | 662.67 | 708.1409 | 693.4449
204 | 663.67 | 715.5959 | 700.8999
205 | 664.67 | 723.1264 | 708.4304
206 | 665.67 | 730.7341 | 716.0381
207 | 666.67 | 738.4209 | 723.7249
208 | 667.67 | 746.1889 | 731.4929
209 | 668.67 | 754.0404 | 739.3444
210 | 669.67 | 761.9779 | 747.2819
211 | 670.67 | 770.0043 | 755.3083
212 | 671.67 | 778.1225 | 763.4265
213 | 672.67 | 786.336 | 771.64
214 | 673.67 | 794.6487 | 779.9527
215 | 674.67 | 803.0651 | 788.3691
216 | 675.67 | 811.5904 | 796.8944
217 | 676.67 | 820.2306 | 805.5346
218 | 677.67 | 828.993 | 814.297
219 | 678.67 | 837.8863 | 823.1903
220 | 679.67 | 846.9215 | 832.2255
221 | 680.67 | 856.1128 | 841.4168
222 | 681.67 | 865.4795 | 850.7835
223 | 682.67 | 875.049 | 860.353
224 | 683.67 | 884.8646 | 870.1686
225 | 684.67 | 895.0064 | 880.3104
226 | 685.67 | 905.6867 | 890.9907
227 | 686.67 | #NUM! | #NUM!
228 | 687.67 | #NUM! | #NUM!
229 | 688.67 | #NUM! | #NUM!
230 | 689.67 | #NUM! | #NUM!
231 | 690.67 | #NUM! | #NUM!
232 | 691.67 | #NUM! | #NUM!
233 | 692.67 | #NUM! | #NUM!
234 | 693.67 | #NUM! | #NUM!